## Sheet1
| Number of crystals |  |  | Power dissipation per channel in W |  |  |  | A.Hormiere
EB | 61200 |  |  | 2 | 0.002 |  |  | ST-CV
EE | 16500 | [6 empty] | 2001-07-09
Safety margin %
15 |  |  |  | Dissipation table in kW | [5 empty] | flow l/s | H in m
[9 empty] | Regulating | 70 | 50 |  | efficiency (rendement)
|  |  |  | Power circuit | EB | EE |  |  | Power | 15 | 50 |  | 0.7
with 1.2W/ch
|  | 73.44 | 20 | VFE | 122.4 | 33
|  | 36 | 10 | LVR | 60 | 16.6667 |  |  |  |  | Regulating | Power
|  | 8.25 | 2.15 | LV cables inside E E/B | 13.75 | 3.5833 |  |  | Power to cool kW |  | 49.05 | 10.5107
|  | 8.7 | 2.3 | LV cb LVR-E E/B | 14.5 | 3.8333
|  | 10.5 | 3 | LV cb inside CMS | 17.5 | 5
|  |  |  | totals LV cables | 45.75 | 12.4167 | 58.1667
|  |  |  | TOTALS | 228.15 | 62.0833 | 290.2333
|  |  |  | Regulating circuit | EB | EE
|  |  |  | VFE | 12.24 | 3.3
|  |  |  | Ambiant | 0.6 | 0
|  |  |  | TOTALS | 12.84 | 3.3 | 16.14
Used ST-CV values (+pump +margin)
[5 empty] | Barrel | Endcaps | Pump | TOTAL
|  |  |  | Ecal Power | 262.3725 | 71.3958 | 10.5107 | 344.279
|  |  |  | Ecal regulating | 14.766 | 3.795 | 49.05 | 67.611